Tuning a proportional-integral-derivative (PID) controller is a matter of selecting the right mix of P, I, and D action to achieve a desired closed performance (see "Basics of Proportional-Integral-Derivative Control," Control Engineering, March 1998).

The ISA standard form of the PID algorithm is:

The variable CO(t) represents the controller output applied to the process at time t, PV(t) is the process variable coming from the process, and e(t) is the error between the setpoint and the process variable. Proportional action is weighted by a factor of P, the integral action is weighted by P/TI, and the derivative action is weighted by PTD where P is the controller gain, TI is the integral time, and TD is the derivative time.

In 1942, John G. Ziegler and Nathaniel B. Nichols of Taylor Instruments (now part of ABB Instrumentation in Rochester, N.Y.) published two techniques for setting P, TI, and TD to achieve a fast, though not excessively oscillatory, closed-loop step response. Their "open loop" technique is illustrated by the reaction curve in the figure. This is a strip chart of the process variable after a unit step has been applied to the process while the controller is in manual mode (i.e., without feedback).

A line drawn tangent to the reaction curve at its steepest point shows how fast the process reacted to the step input. The inverse of this line's slope is the process time constant T. The reaction curve also shows how long the process waited before reacting to the step (the deadtime d) and how much the process variable increased relative to the size of the step (the process gain K). Ziegler and Nichols determined that the best settings for the tuning parameters could be computed from T, d, and K as follows:

Once these parameter values are loaded into the PID algorithm and the controller is returned to automatic mode, subsequent changes in the setpoint should produce the desired "not-too-oscillatory" closed-loop response. A controller thus tuned should also be able to reject load disturbances quickly with only a few oscillations in the process variable.

Ziegler and Nichols also described a "closed loop" tuning technique that is conducted with the controller in automatic mode (i.e., with feedback), but with the integral and derivative actions shut off. The controller gain is increased until any disturbance causes a sustained oscillation in the process variable. The smallest controller gain that can cause such an oscillation is called the ultimate gain Pu. The period of those oscillations is called the ultimate period Tu. The appropriate tuning parameters can be computed from these two values according to these rules:

A reprint of Ziegler and Nichols' 1942 paper can be found in "Reference Guide to PID Tuning" (Control Engineering, 1991). Note, however that the tuning rules given in that paper differ from those shown here because Ziegler and Nichols were working with a slightly different form of the PID algorithm. Different PID controllers use different algorithms, and each must be tuned according to the appropriate set of rules. The Rules also change when the derivative or the integral action is disabled.

Ultimate Sensitivity Method
The goal is to achieve a marginally stable controller response
(see marginally stable response chart)

Closed Loop (Loop in Automatic) Test 1

- Choose any GAIN setting. Place INTEGRAL at maximum time (smallest value) and place DERIVATIVE at minimum value or turn it completely off.

- Make a 10% change in SETPOINT (SP).

- Record the PROCESS VARIABLE (PV) and CONTROLLER OUTPUT (CO) responses. (If process becomes unstable, place the loop in MANUAL and do what is needed to maintain control.)

- If recorded response produces a stable (lagging) response, proceed to Test 2.

- If recorded response produces an unstable (leading) response, proceed to Test 3.

Test 2

- Double the GAIN setting (Leave INTEGRAL and DERIVATIVE the same as Test 1).

- Make a 10% change in SP.

- Record the PV and CO responses. (If process becomes unstable, place the loop in MANUAL and do what is needed to maintain control.)

- If recorded response produces a stable (lagging) response, repeat Test 2.

- If recorded response produces an unstable (leading) response, proceed to Test 3.

Test 3

- Half the GAIN setting (Leave INTEGRAL and DERIVATIVE the same as Test 1 and 2).

- Make a 10% change in SP.

- Record the PV and CO responses. (If process becomes unstable, place the loop in MANUAL and do what is needed to maintain control.)

- If recorded response produces a stable (lagging) response, proceed to Test 2.

- If recorded response produces an unstable (leading) response, repeat Test 3.

Repeat testing until a marginally stable response has been recorded.